## Лист1
Сведения о наличии мощности, свободной для технологического присоединения к электрическим сетям ООО "Энергонефть Томск" по состоянию на 2 квартал 2013г.
№ п.п. | Наименование подстанции | Напряжение обмоток, кВ | Трансформаторы |  |  |  | % загрузки ПС (при ремонте одного тр-ра) | Текущий резерв мощности для присоединения потребителей (по результатам контрольного замера зима 2013 г.) (МВт) резервная мощность с учетом выданных ТУ | Текущий резерв мощности для присоединения потребителей (по вышестоящей сетевой организации (МВт) резервная мощность | Примечание, Ссылка на информационный ресурс ОАО «ТРК», ФСК «ЕЭС»
|  |  | Мощность номинальная 1Т (МВА) | Мощность фактическая 1Т (МВА) | Мощность номинальная 2Т (МВА) | Мощность фактическая 2Т (МВА) | #VALUE! | #VALUE! | #VALUE!
1 | Новый Васюган | 110/10 | 6,3 | 0,7 | 6,3 | 0,7 | #VALUE! | #VALUE! | 0 | http://www.trk.tom.ru/module/?id=350
2 | Катыльгинская | 110/35/6 | 25 | 8.5 | 25 | 6.3 | 59.2 | 17.6 | 0 | http://www.trk.tom.ru/module/?id=350
3 | Крапивинская | 110/35/6 | 25 | 15.2 | 25 | 16.8 | 128 | 0 | 0 | http://www.trk.tom.ru/module/?id=350
4 | Двуреченская | 110/35/6 | 25 | 6.5 | 25 | 8 | 58 | 17.75 | 0 | http://www.trk.tom.ru/module/?id=350
5 | Западно-Моисеевская | 110/35/6 | 25 | 8 | 25 | 9 | 68 | 16.5 | 0 | http://www.trk.tom.ru/module/?id=350
6 | Черемшанская | 3Т 110/35/6 | 16 | 5.8 |  |  | 36.25 | 5.1 | 0 | http://www.trk.tom.ru/module/?id=350
7 | Черемшанская | 35/6 | 10 | 3 | 10 | 4.3 | 73 | 6.35 | 0 | http://www.trk.tom.ru/module/?id=350
8 | Игольская | 110 | 25 | 8 | 25 | 10 | 72 | 16 | 0 | http://www.trk.tom.ru/module/?id=350
9 | Григорьевская | 110/35/6 | 16 | 3.5 | 16 | 4.5 | 50 | 12 | 0 | http://www.trk.tom.ru/module/?id=350
10 | №101 | 35/6 | 4 | 1.1 | 4 | 0.9 | 50 | 3 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
11 | №102 | 35/6 | 6.3 | 0.6 | 6.3 | 1.5 | 33.3333 | 5.25 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
12 | №103 | 35/6 | 16 | 4 | 16 | 4 | 50 | 12 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
13 | №104 | 35/6 | 6.3 | 2.7 | 6.3 | 1.8 | 71.4286 | 4.05 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
14 | №105 | 35/6 | 6.3 | 2.8 | 6.3 | 1.8 | 73.0159 | 4 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
15 | №106 | 35/6 | 4 | 0.55 | 4 | 0.32 | 21.75 | 3.565 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
16 | №107 | 35/6 | 10 | 1.7 | 10 | 3.6 | 53 | 7.35 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
17 | №108 | 35/6 | 6.3 | 1.4 | 6.3 | 1.7 | 49.2063 | 4.75 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
18 | №109 | 35/6 | 6.3 | 2.9 | 6.3 | 1 | 61.9048 | 4.35 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
19 | №110 | 35/6 | 6.3 | 1.4 | 6.3 | 1.7 | 49.2063 | 4.75 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
20 | №111 | 35/6 | 4 | 0.9 | 4 | 0.9 | 45 | 3.1 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
21 | №112 | 35/6 | 4 | 0.6 | 4 | 0.3 | 22.5 | 3.55 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
22 | №113 | 35/6 | 4 | 1.2 | 4 | 0.4 | 40 | 3.2 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
23 | №114 | 35/6 | 4 | 1 | 4 | 1.6 | 65 | 2.7 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
24 | №115 | 35/6 | 2.5 | 0.45 | 1.6 | 0.15 | 24 | 1.75 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
25 | №123 | 35/6 | 10 | 3.5 | 10 | 3.4 | 69 | 0 |  | Центр питания закрыт из-за пропускной способности ВЛ-35 кВ
26 | №124 | 35/6 | 10 | 2.5 | 10 | 1.9 | 44 | 0 |  | Центр питания закрыт из-за пропускной способности ВЛ-35 кВ
27 | №125 | 35/6 | 4 | 0.7 | 4 | 0.3 | 25 | 3.5 | 5.8 | http://www.trk.tom.ru/module/?id=350
28 | №126 | 35/6 | 10 | 0.6 | 10 | 3.1 | 37 | 8.15 |  | http://www.trk.tom.ru/module/?id=350
29 | №127 | 35/6 | 16 | 0.7 | 16 | 0.7 | 8.75 | 3.8 |  | Ограничение мощности из-за пропускной способности КЛ-6 кВ
30 | №128 | 35/6 | 10 | 0.6 | 10 | 0.6 | 12 |  |  | Ограничение мощности из-за пропускной способности КЛ-6 кВ
31 | №129 | 35/6 | 1.6 | 0.4 | 1.6 | 0.2 | 37.5 | 0 |  | Центр питания закрыт из-за пропускной способности ВЛ-35 кВ
32 | №130 | 35/6 | 4 | 0.6 | 6.3 | 0.4 | 25 | 4.65 | 0 | http://www.trk.tom.ru/module/?id=350
33 | №201 | 35/6 | 4 | 1 | 4 | 0.2 | 30 | 3.4 | 0 | http://www.trk.tom.ru/module/?id=350
34 | №202 | 35/6 | 6.3 | 5.2 | 6.3 | 0 | 82.5397 | 3.7 | 0 | http://www.trk.tom.ru/module/?id=350
35 | №203 | 35/6 | 6.3 | 1.4 | 6.3 | 0.4 | 28.5714 | 5.4 | 0 | http://www.trk.tom.ru/module/?id=350
36 | №204 | 35/6 | 6.3 | 4 | 6.3 | 0.4 | 69.8413 | 4.1 | 0 | http://www.trk.tom.ru/module/?id=350
37 | №205 | 35/6 | 6.3 | 2.7 | 6.3 | 2.3 | 79.3651 | 3.8 | 0 | http://www.trk.tom.ru/module/?id=350
38 | №206 | 35/6 | 10 | 1.6 | 10 | 1 | 26 | 8.7 | 0 | http://www.trk.tom.ru/module/?id=350
39 | №207 | 35/6 | 10 | 1.6 | 10 | 1.8 | 34 | 8.3 | 0 | http://www.trk.tom.ru/module/?id=350
40 | №208 | 35/6 | 6.3 | 0.8 | 6.3 | 0.4 | 19.0476 | 5.7 | 0 | http://www.trk.tom.ru/module/?id=350
41 | №302 | 35/6 | 6.3 | 0.33 | 6.3 | 0.1 | 6.8254 | 6.085 | 0 | http://www.trk.tom.ru/module/?id=350
42 | №303 | 35/6 | 10 | 2.2 | 10 | 0.35 | 25.5 | 8.725 | 0 | http://www.trk.tom.ru/module/?id=350
43 | №304 | 35/6 | 4 | 1 | 4 | 1.2 | 55 | 2.9 | 0 | http://www.trk.tom.ru/module/?id=350
44 | №305 | 35/6 | 6.3 | 0.8 | 6.3 | 1 | 28.5714 | 5.4 | 0 | http://www.trk.tom.ru/module/?id=350
45 | №306 | 35/6 | 2.5 | 0.75 | 2.5 | 0.75 | 60 | 1.75 | 0 | http://www.trk.tom.ru/module/?id=350
46 | №307 | 35/6 | 10 | 2.5 | 10 | 1 | 35 | 8.25 | 0 | http://www.trk.tom.ru/module/?id=350
47 | №308 | 35/6 | 10 | 0.7 | 10 | 1.6 | 23 | 8.85 | 0 | http://www.trk.tom.ru/module/?id=350
48 | №401 | 35/6 | 6.3 | 1.3 | 6.3 | 1 | 36.5079 | 5.15 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
49 | №402 | 35/6 |  |  | 4 | 0.4 | - | 1.8 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
50 | №403 | 35/6 | 4 | 0.25 | 4 | 0.15 | 10 | 3.8 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
51 | №404 | 35/6 | 4 | 0.1 | 4 | 0.5 | 15 | 3.7 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
52 | №405 | 35/6 | 2.5 | 0.25 | 4 | 1 | 50 | 2.625 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
53 | №407 | 35/6 | 4 | 0.3 | 4 | 0.25 | 13.75 | 3.725 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
54 | №409 | 35/6 | 4 | 0.7 | 6.3 | 1.4 | 52.5 | 4.1 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
55 | №410 | 35/6 | 6.3 | 0.9 | 4 | 0.4 | 20.6349 | 4.5 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
56 | №412 | 35/6 | 6.3 | 0.5 | 6.3 | 1.7 | 34.9206 | 5.2 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
57 | №414 | 35/6 | 6.3 | 1.6 | 4 | 0.7 | 36.5079 | 4 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
58 | №415 | 35/6 | 4 | 0.05 | 4 | 0.3 | 8.75 | 3.825 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
59 | №417 | 35/6 | 6.3 | 2 | 6.3 | 0.5 | 39.6825 | 5.05 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
60 | №418 | 35/6 | 6.3 | 0.05 | 6.3 | 0.4 | 7.1429 | 6.075 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
61 | №420 | 35/6 | 4 | 0.7 | 4 | 0.7 | 35 | 3.3 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
62 | №421 | 35/6 | 10 | 1 | 10 | 2.2 | 32 | 8.4 | 0 | http://www.fsk-ees.ru/consumers/disclosures_in_accordance_with_government_decree_of_21_01_2004_24/obem_svobodnoy_transformatornoy_moshchnosti/
63 | №501 | 35/6 | 6.3 | 1.8 | 6.3 | 1.95 | 59.5238 | 4.425 | 0 | http://www.trk.tom.ru/module/?id=350
64 | №502 | 35/6 | 4 | 0.65 | 4 | 0.64 | 32.25 | 3.355 | 0 | http://www.trk.tom.ru/module/?id=350
65 | №503 | 35/6 | 6.3 | 0.4 | 6.3 | 1.6 | 31.746 | 5.3 | 0 | http://www.trk.tom.ru/module/?id=350
66 | №516 | 35/6 | 6.3 | 1.2 | 6.3 | 0.4 | 25.3968 | 5.5 | 0 | http://www.trk.tom.ru/module/?id=350
67 | №524 | 35/6 | 4 | 0.2 | 4 | 0.35 | 13.75 | 3.725 | 0 | http://www.trk.tom.ru/module/?id=350
68 | №548 | 35/6 | 4 | 0.3 | 2.5 | 0 | 7.5 | 3.1 | 0 | http://www.trk.tom.ru/module/?id=350
69 | №558 | 35/6 | 6.3 | 0.9 | 6.3 | 2 | 46.0317 | 4.85 | 0 | http://www.trk.tom.ru/module/?id=350
70 | №601 | 35/6 | 10 | 3.9 | 10 | 2.7 | 66 | 6.7 | 0 | http://www.trk.tom.ru/module/?id=350
71 | №602 | 35/6 | 10 | 0.8 | 10 | 1.4 | 22 | 8.9 | 0 | http://www.trk.tom.ru/module/?id=350
72 | №603 | 35/6 | 6.3 | 1 | 6.3 | 0.8 | 28.5714 | 5.4 | 0 | http://www.trk.tom.ru/module/?id=350
73 | №604 | 35/6 | 6.3 | 0.2 | 6.3 | 3.7 | 61.9048 | 4.35 | 0 | http://www.trk.tom.ru/module/?id=350
74 | №605 | 35/6 | 10 | 1.8 | 10 | 4.2 | 60 | 7 | 0 | http://www.trk.tom.ru/module/?id=350
75 | №606 | 35/6 | 2.5 | 0.45 | 2.5 | 0.45 | 36 | 2.05 | 0 | http://www.trk.tom.ru/module/?id=350
76 | №607 | 35/6 | 6.3 | 0.05 | 6.3 | 0.6 | 10.3175 | 5.975 | 0 | http://www.trk.tom.ru/module/?id=350
77 | №608 | 35/6 | 6.3 | 1.2 | 6.3 | 1.8 | 47.619 | 4.8 | 0 | http://www.trk.tom.ru/module/?id=350
78 | №609 | 35/6 | 6.3 | 2.4 | 6.3 | 2.3 | 74.6032 | 3.95 | 0 | http://www.trk.tom.ru/module/?id=350
79 | №610 | 35/6 | 6.3 | 0.9 | 6.3 | 0.8 | 26.9841 | 5.45 | 0 | http://www.trk.tom.ru/module/?id=350
80 | №611 | 35/6 | 10 | 1.5 | 10 | 1.7 | 32 | 8.4 | 0 | http://www.trk.tom.ru/module/?id=350